{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Quote","MCC Info"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Quote","index":0,"n_rows":108,"n_cols":10,"rows_kept":108,"cut":false,"hidden":false,"merged":[[0,5,1,8],[106,2,106,8],[104,2,104,8],[103,2,103,8],[10,1,10,2],[10,4,10,7],[11,1,11,2],[11,4,11,7],[12,1,12,2],[12,4,12,7],[13,1,13,2],[13,4,13,7],[14,1,14,2],[14,4,14,7],[4,2,4,3],[6,1,6,2],[6,4,6,7],[7,1,7,2],[7,4,7,7],[8,1,8,2],[8,4,8,7],[9,1,9,2],[9,4,9,7],[16,4,16,7],[17,1,17,2],[17,4,17,7],[18,1,18,2],[18,4,18,7],[19,1,19,2],[19,4,19,7],[15,1,15,2],[15,4,15,7],[16,1,16,2],[20,1,20,2],[20,4,20,7],[21,1,21,2],[21,4,21,7],[22,1,22,2],[22,4,22,7],[23,1,23,2],[23,4,23,7],[24,1,24,2],[24,4,24,7],[25,1,25,2],[25,4,25,7],[26,1,26,2],[26,4,26,7],[27,1,27,2],[27,4,27,7],[28,1,28,2],[28,4,28,7],[29,1,29,2],[29,4,29,7],[30,1,30,2],[30,4,30,7],[31,1,31,2],[31,4,31,7],[32,1,32,2],[32,4,32,7],[33,1,33,2],[33,4,33,7],[34,1,34,2],[34,4,34,7],[35,1,35,2],[35,4,35,7],[36,1,36,2],[36,4,36,7],[37,1,37,2],[37,4,37,7],[38,1,38,2],[38,4,38,7],[39,1,39,2],[39,4,39,7],[40,1,40,2],[40,4,40,7],[64,2,64,8],[47,1,47,5],[47,6,47,7],[41,1,41,2],[41,4,41,7],[42,1,42,2],[42,4,42,7],[43,1,43,2],[43,4,43,7],[44,1,44,2],[44,4,44,7],[45,1,45,2],[45,4,45,7],[56,2,56,8],[58,2,58,8],[59,2,59,8],[60,2,60,8],[61,2,61,8],[62,2,62,8],[63,2,63,8],[46,1,46,5],[46,6,46,7],[53,2,53,8],[54,2,54,8],[55,2,55,8],[76,2,76,8],[77,2,77,8],[78,2,78,8],[79,2,79,8],[80,2,80,8],[81,2,81,8],[74,2,74,8],[75,2,75,8],[82,2,82,8],[65,2,65,8],[66,2,66,8],[67,2,67,8],[68,2,68,8],[69,2,69,8],[70,2,70,8],[71,2,71,8],[72,2,72,8],[73,2,73,8],[2,2,2,9],[3,2,3,9],[101,2,101,8],[48,1,48,5],[48,6,48,7],[57,2,57,8],[92,2,92,8],[93,2,93,8],[94,2,94,8],[95,2,95,8],[96,2,96,8],[97,2,97,8],[98,2,98,8],[99,2,99,8],[100,2,100,8],[83,2,83,8],[84,2,84,8],[85,2,85,8],[86,2,86,8],[87,2,87,8],[88,2,88,8],[89,2,89,8],[90,2,90,8],[91,2,91,8]]}
[null,null,null,null,null,"\n18805 Adams Ct. #110\n Morgan Hill, CA 95037 USA\n866-washlink / +1-408-924-0808"]
[null,null,null,null,null,null,null,null,null,{"$f":"NOW()","v":"2017-05-04T08:13:45.200"}]
[null,"prepared for:","Your Car Wash"]
["Qty",null,"WASHLINK SYSTEMS MOTOR CONTROL CENTER FULL LOAD AMPS"]
[null,"Voltage?","460/480vac"]
["Mtr","Type",null,"HP",null,"Name"]
[1,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[2,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[3,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[4,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[5,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[6,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[7,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[8,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[9,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[10,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[11,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[12,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[13,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[14,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[15,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[16,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[17,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[18,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[19,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[20,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[21,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[22,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[23,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[24,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[25,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[{"$f":"A31+1","v":26},"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[{"$f":"A32+1","v":27},"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[{"$f":"A33+1","v":28},"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[29,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[30,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[31,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[32,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[33,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[34,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[35,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[36,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[37,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[38,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[39,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[40,"Choose HP",null,"?",null,null,null,null,null,"AMPS"]
[0,"Enter description here",null,null,null,null,0,null,{"$f":"A47*G47","v":0},"AMPS"]
[0,"Enter description here",null,null,null,null,0,null,{"$f":"A48*G48","v":0},"AMPS"]
[0,"Enter description here",null,null,null,null,0,null,{"$f":"A49*G49","v":0},"AMPS"]
[null,null,null,null,null,null,null,null,"MCC FLA",{"$f":"SUM(I7:I49)","v":0}]
[null,null,"Typical Main Breaker Sizes",null,null,null,null,null,"25% of FLA",{"$f":"J50*0.25","v":0}]
[null,"100, 125, 150, 200, 225, 250, 300, 400, 600, 800 amp",null,null,null,null,null,null,"Required Power",{"$f":"SUM(J50:J51)","v":0}]
[]
[null,"MCC Notes:"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Accepted by:","Name:__________________________________________Date:_______________"]
[]
[null,null,"Signature:___________________________________________________________"]
[null,"This is for planing only!  Actual drawings will be provided with deposited order."]

{"sheet":"MCC Info","index":1,"n_rows":88,"n_cols":11,"rows_kept":88,"cut":false,"hidden":true,"merged":[]}
["HP",208,230,"380-400",460,"575-600","SMARTLink","Across the Line"]
[0.5,2.4,2.2000000000000002,1.3,1.1000000000000001,0.9,"HP","208-240","380-415","460-480"]
[1,4.5999999999999996,4.2,2.2999999999999998,2.1,1.7,1,{"$f":"B3+125","v":129.6},{"$f":"C3+125","v":129.19999999999999},{"$f":"E3+125","v":127.1}]
[1.5,6.6,6,3.3,3,2.4,1.5,{"$f":"B4+125","v":131.6},131,128]
[2,7.5,6.8,4.3,3.4,2.7,2,132.5,131.80000000000001,128.4]
[3,10.6,9.6,6.1,4.8,3.9,3,135.6,134.6,129.80000000000001]
[5,16.7,15.2,9.6999999999999993,7.6,6.1,5,141.69999999999999,140.19999999999999,132.6]
[7.5,24.2,22,14,11,9,7.5,149.19999999999999,147,136]
[10,30.8,28,18,14,11,10,155.80000000000001,153,139]
[15,46.2,42,27,21,17,15,171.2,167,146]
[20,59.8,54,34,27,22,20,184.8,179,152]
[25,74.8,68,44,34,27,25,199.8,193,159]
[30,88,80,51,40,32,30,213,205,165]
[40,114,104,66,52,41]
[50,143,130,83,65,52]
[60,169,154,103,77,62]
[]
[]
[]
[]
[null,"Soft Starter"]
["HP","208-240","380-415","460-480","575-600",null,"HP","208-240","380-415","460-480"]
[1,{"$f":"B3+700","v":704.6},704.2,{"$f":"E3+700","v":702.1},701.7,null,1,{"$f":"B23+125","v":829.6},{"$f":"C23+125","v":829.2},{"$f":"D23+125","v":827.1}]
[1.5,706.6,706,703,702.4,null,1.5,831.6,831,828]
[2,707.5,706.8,703.4,702.7,null,2,832.5,831.8,828.4]
[3,710.6,709.6,704.8,703.9,null,3,835.6,834.6,829.8]
[5,716.7,715.2,707.6,706.1,null,5,841.7,840.2,832.6]
[7.5,724.2,722,711,709,null,7.5,849.2,847,836]
[10,{"$f":"B9+1700","v":1730.8},{"$f":"C9+700","v":728},714,711,null,10,1855.8,853,839]
[15,{"$f":"B10+1700","v":1746.2},742,721,717,null,15,1871.2,867,846]
[20,{"$f":"B11+1700","v":1759.8},{"$f":"C11+1100","v":1154},{"$f":"E11+1100","v":1127},1122,null,20,1884.8,1279,1252]
[25,{"$f":"B12+1700","v":1774.8},1168,1134,1127,null,25,1899.8,1293,1259]
[30,{"$f":"B13+1700","v":1788},1180,1140,1132,null,30,1913,1305,1265]
[]
[]
[]
[]
[]
[]
[]
[null,"VFD's"]
["HP","208-240","380-415","460-480","575-600",null,"HP","208-240","380-415","460-480"]
[1,{"$f":"B3+1100","v":1104.5999999999999},{"$f":"C3+1300","v":1304.2},{"$f":"E3+1300","v":1302.0999999999999},{"$f":"F3+2600","v":2601.6999999999998},null,1,{"$f":"B43+125","v":1229.5999999999999},{"$f":"C43+125","v":1429.2},{"$f":"D43+125","v":1427.1}]
[1.5,{"$f":"B4+1100","v":1106.5999999999999},1306,{"$f":"E4+1300","v":1303},{"$f":"F4+2600","v":2602.4},null,1.5,1231.5999999999999,1431,1428]
[2,{"$f":"B5+1100","v":1107.5},1306.8,{"$f":"E5+1300","v":1303.4000000000001},{"$f":"F5+2600","v":2602.6999999999998},null,2,1232.5,1431.8,1428.4]
[3,{"$f":"B6+1100","v":1110.5999999999999},{"$f":"C6+1500","v":1509.6},{"$f":"E6+1500","v":1504.8},{"$f":"F6+3000","v":3003.9},null,3,1235.5999999999999,1634.6,1629.8]
[5,{"$f":"B7+1400","v":1416.7},{"$f":"C7+1700","v":1715.2},{"$f":"E7+1700","v":1707.6},{"$f":"F7+3400","v":3406.1},null,5,1541.7,1840.2,1832.6]
[7.5,{"$f":"B8+1450","v":1474.2},{"$f":"C8+1700","v":1722},{"$f":"E8+1700","v":1711},{"$f":"F8+3400","v":3409},null,7.5,1599.2,1847,1836]
[10,{"$f":"B9+1500","v":1530.8},{"$f":"C9+1800","v":1828},{"$f":"E9+1800","v":1814},{"$f":"F9+3600","v":3611},null,10,1655.8,1953,1939]
[15,{"$f":"B10+2100","v":2146.1999999999998},{"$f":"C10+2100","v":2142},{"$f":"E10+2100","v":2121},{"$f":"F10+4200","v":4217},null,15,2271.1999999999998,2267,2246]
[20,{"$f":"B11+2500","v":2559.8000000000002},{"$f":"C11+2600","v":2654},{"$f":"E11+2600","v":2627},{"$f":"F11+5200","v":5222},null,20,2684.8,2779,2752]
[25,{"$f":"B12+2600","v":2674.8},{"$f":"C12+3300","v":3368},{"$f":"E12+3300","v":3334},{"$f":"F12+6600","v":6627},null,25,2799.8,3493,3459]
[30,{"$f":"B13+7000","v":7088},{"$f":"C13+7500","v":7580},{"$f":"E13+7500","v":7540},{"$f":"F13+15000","v":15032},null,30,7213,7705,7665]
[]
[]
[]
[null,"Breaker Only"]
["HP"]
[1,300]
[1.5,300]
[2,300]
[3,300]
[5,400]
[7.5,400]
[10,400]
[15,600]
[20,700]
[25,900]
[30,1100]
[]
[]
[null,"HP"]
[null,"?",null,"Voltage",null,"Control Voltage",null,"Type",null,null,"SMARTLink"]
[null,0.5,null,"Choose",null,"Choose",null,"Choose Type",null,null,"No"]
[null,1,null,"208vac",null,"24vac",null,"Choose HP",null,null,"Yes"]
[null,1.5,null,"230/240vac",null,"24vdc",null,"Soft Starter"]
[null,2,null,"380/400vac",null,"110vac",null,"Variable Frequency Drive"]
[null,3,null,"460/480vac",null,"220vac",null,"Breaker Only"]
[null,5,null,"575vac"]
[null,7.5]
[null,10,null,"Chose"]
[null,15]
[null,20]
[null,25]
[null,30]
[null,40]
[null,50]
[null,60]